# Procedure | Canberra Health Services

## Infection Prevention and Control risk assessment and action plan for all construction and maintenance activities

CHS25/356

Contents

Purpose	2

Scope	2

Section 1 – Construction activity risk identification	3

Section 2 – Determine class of controls	5

Section 3 – Harmful Pathogens	14

Section 4 – Management of Mould	15

Section 5 – Microbial and air particle sampling	19

Section 6 – Record Management	22

Evaluation	22

Related policies, procedures, guidelines and legislation	22

References	23

Definition of terms	24

Search terms	25

Attachments	25

Attachment 1 – IPCRA – Prior to Construction	27

Attachment 2 – IPCRA – Site Inspection Record	31

Attachment 3 – IPCRA – End of Construction Checklist	33

Attachment 4 – Weekly Flushing Schedule	35

Attachment 5 – Water Sampling Information Guide	36

#### Purpose

The purpose of this procedure is to provide guidance and direction for all personnel involved in construction and maintenance activities across CHS. It aims to ensure that all activities are conducted safely and appropriately, minimising the risk of infection to patients, visitors, contractors, and staff 2.

Construction and maintenance activities across health facilities require expert planning, coordination and management to reduce the risk of pathogen disruption and transmission to humans.

This procedure aligns with information contained within the Australasian Health Facility Guidelines (AusHFG) and Work Health and Safety Management System for Canberra Health Services (CHS). In accordance with the Public Health Act 1997, and the Health Facility Code of Practice 2021 (the code), CHS will align practice to meet the requirements outlined in the AusHFG when planning and implementing construction works. The AusHFG recommends an Infection Prevention and Control professional is involved at all stages of the construction project lifecycle 1.

Back to Contents

#### Scope

This procedure applies to all CHS healthcare facilities where renovation, maintenance, demolition, and construction activities take place. The type of construction and the population at risk, will determine the necessary class of controls required (or to be implemented).

Environmental disturbances that occur during construction or renovation activities pose both airborne and waterborne risks, particularly to persons who are immunocompromised or at great risk of infection.

It is essential that Infection Prevention and Control (IPAC), Infrastructure Safety and Risk (ISAR) or North Canberra Hospital equivalent, project stakeholders and the relevant clinical areas are included in all stages of construction to minimise the risk of infection to vulnerable persons in a healthcare facility.

This procedure applies to all CHS staff and contracted staff working across the CHS network. CHS network includes Canberra Hospital, Clare Holland House, North Canberra Hospital, University of Canberra Hospital and community-based services.

Back to Contents

#### Section 1 – Construction activity risk identification

Construction activities can range from minor (e.g., wiring for communication equipment) to major (e.g., projects involving the demolition and construction of new buildings). All such activities must adhere to current legislative requirements, Australian Standards and Codes of Practice. Any CHS staff member designated as a Health Project Representative (HPR) must complete the mandatory training coordinated by ISAR (or NCH equivalent). Trained HPRs are responsible for identifying, analysing, and managing risks to minimise potential harm.

##### 1.1 Construction site Infection Prevention and Control Risk Assessment (IPCRA) Pre-Construction

Before construction activities begin, an Infection Prevention and Control Risk Assessment (IPCRA) must be completed (Attachment 1). This is to ensure the construction zone is correctly prepared with control measures to minimise the infection risk to patients, staff, contractors and visitors from construction activities. In some cases, it may be beneficial to conduct the IPCRA – Pre-construction, prior to the building tender being released. This will allow for contractors to include costs for complying with IPCRA into their budget.

Midway through construction activities, or at specific staging intervals, the construction site and adjacent areas will be reviewed, as per the IPCRA Site Inspection Record (Attachment 2). These regular assessments of the construction zone and adjacent areas will inform the project team whether current infection control measures are adequate or need further controls in place to reduce the potential for harm.

At completion of construction activities and prior to handover, the IPCRA End of Construction Checklist (Attachment 3) is undertaken to ensure the area is safe for reoccupation.

For Class I and II control activities the HPR of the area is to conduct the IPCRA Pre-Construction for review by IPAC.  IPAC will determine the requirement for environmental monitoring, Site Inspection Record and End of Construction Checklist. The construction works may be considered so minor that they are not necessary.

All Class III and Class IV control measure activities require an IPAC and/or ISAR (or NCH equivalent) representative to undertake the Pre-Construction IPCRA Risk Assessment, IPCRA Site Inspection and IPCRA End of Construction Checklist in collaboration with the HPR and Contractor’s representative. The IPCRA’s are separate to the CHS project defect sign off required for commissioning activities.

The IPCRA action plan will address:

The extent of construction work

The identification of the patient population at risk

The location of the patient population in relation to the construction site

Ventilation system types and potential impact

Determination of air monitoring requirements, including methodology and frequency

Paths of travel for contractors, construction materials and waste

High risk contaminants and/or location of:

Water damage

Ceiling dust

Service shafts especially in the presence of unexpected moisture

Sprayed on fire retardants

##### 1.2 Infection prevention and control recommendations during construction activities

All Contractors are required to complete the CHS Contractor Induction package prior to attending any CHS site. This induction includes an Infection Prevention and Control module, which must be completed for site entry.

Recommendations include, but not limited to:

Ensuring works comply with assigned control measures as per IPCRA

Escalation pathways are identified between contractors and CHS stakeholders

Hoarding/physical barriers must be maintained throughout all activities. Hoardings are to be regularly monitored by the project manager to ensure the hoarding is appropriate for the location and ventilation systems, and there is no impact to fire protection systems i.e. sprinklers or fire, smoke and heat detectors

##### 1.3 End of construction

Prior to handover it is the responsibility of the contractor to ensure the area complies with the standards for occupation. This includes, but not limited to:

All surfaces including walls, ceilings, windows, ventilation systems, service cavities and ceiling spaces have been thoroughly cleaned

All surfaces and joins are free from gaps. In clinical areas, surfaces should be smooth and impervious to liquids

Water from taps installed to be visibly assessed for laminar flow and fitted without aerators

Water flow from taps should not flow directly into the drain as this can aerosolise bacteria from the drain

Isolation rooms are operating as designed (e.g. supply air, air changes, exhaust, seals and gauges)

Air sampling and particle counts have been conducted, when deemed necessary by IPAC and Canberra Hospital Mould Working Group (or NCH equivalent) and returned results within defined limits.

Recertification of HEPA filters, laminar flow cabinets and laminar/clean flow systems installed.

Back to Contents

#### Section 2 – Determine class of controls

The CHS IPCRA is adapted from Part D of the AusHFG and comprises of four steps to determine the class of control required 1.

Step 1: Determine the type of construction activity, refer to Table 1

Step 2: Determine the patient /persons at risk locations, refer to Table 2

Step 3: Identify the level of controls required by classification (Class I-IV) refer to Table 3

Step 4: Determine infection control measures required to minimise risk due to construction activities according to classification

##### Step 1 - Determine the type of construction activity

Classification of Construction Activities

| Type | Description |
| --- | --- |
| Type A Inspections and general upkeep activities | Includes but not limited to: - removal of ceiling tiles for visual inspection (limited to one tile per 5m2) - painting (but not sanding) - installation of wall covering - minor electrical wiring - minor plumbing - any activities that do not generate dust or require cutting into walls or access to ceiling other than for visual inspection |
| Type B Small scale, short duration activities and which create minimal dust | Includes, but is not limited to: - installation of telephone and computer cabling - access to cavity spaces - cutting into walls or ceiling where dust migration can be controlled |
| Type C Any work that generates a moderate to high level of dust | Includes, but is not limited to: - demolition or removal of built-in building components or assemblies - sanding of walls for painting or wall covering - removal of floor covering/wallpaper, ceiling tiles and casework - new wall construction - minor ductwork or electrical work above ceiling - major cabling activities |
| Type D Major demolition and construction projects | Includes, but are not limited to: - heavy demolition - removal of a complete ceiling system - new construction |

##### Step 2 – Determine the infection control risk group

Risk Group by Location

| Risk | Location |
| --- | --- |
| Low Risk | Office areas |
|  | Non-clinical areas |
|  | Non patient/low risk areas not listed elsewhere |
| Medium Risk | Allied health areas – Physiotherapy, Podiatry, Prosthetics, Speech Pathology, Occupational Therapy, Nutrition, Rehabilitation Unit |
|  | Laundry |
|  | Cafeteria /catering services (kitchens) |
|  | Admissions/Discharge |
|  | MRI |
|  | Nuclear medicine |
|  | Echocardiogram |
|  | Laboratories other than Microbiology or Virology |
|  | Public corridors used by patients and to transport linen and supplies |
|  | Private consulting rooms |
|  | Mental Health services |
| Medium - High Risk | Emergency Department |
|  | Medical Imaging – General |
|  | High Dependency Unit |
|  | Paediatrics (excluding PICU) |
|  | Microbiology laboratories |
|  | Long stay sub-acute units |
|  | Medical and Surgical wards |
|  | Pharmacy - Primary |
|  | Endoscopy/ Bronchoscopy |
|  | Haemodialysis and Peritoneal Dialysis |
|  | Labour and Delivery suites |
|  | Newborn Nurseries |
|  | Recovery/PACU |
| Highest Risk | Oncology Units/Clinical areas caring for immunocompromised patients |
|  | Haematology Units/Clinical areas caring for immunocompromised patients |
|  | Radiation and Chemotherapy outpatients |
|  | Transplant Units |
|  | Pharmacy- Admixture/Cleanrooms |
|  | Operating rooms |
|  | Sterile supply units |
|  | Cardiac catheterisation |
|  | Interventional Radiology/Angiography/Hybrid suites |
|  | Outpatient invasive procedure rooms- i.e. Medical Imaging |
|  | Anaesthetic and pump rooms |
|  | ICU/NICU/PICU |

##### Step 3 – Identify the construction controls required (Class I-IV)

Match the construction activity type (A, B, C, D) determined in Table 1 with the infection control risk group in Table 2 (low, medium, medium-high, highest) to ascertain the Class of Controls (I, II, III, IV) required in Table 3.

Stratification Matrix

|  |  |  | - Type of Construction Activity |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | - Type A | - Type B | - Type C | - Type D |
| - Patient/Person - Location Risk Group | - Low Risk | - I | - II | - II | - III / IV |
|  | - Medium Risk | - I | - II | - III | - IV |
|  | - Medium to High Risk | - I | - III | - III / IV | - IV |
|  | - Highest Risk | - III | - III / IV | - III / IV | - IV |

Example

Intensive Care Unit requires 20m of cabling to be installed in the ceiling for upgrade of IT systems. You are the Project Manager of the activity to install cables in the ICU ceiling. There are 3 firewalls that will require some drilling through to run the cables.

Step 1- The Type of construction is small but drilling through fire walls will cause a moderate level of dust = Type C

Step 2- ICU is the Location and ventilated patients are the Risk Group= Highest Risk

Step 3- Identify the “class of controls” - Highest Risk + Type C = Class III/IV

Infection Prevention and Control and Infrastructure, Safety and Risk Units will apply Class III/IV precautions and complete the Risk Assessment

##### Step 4 – Determine infection control measures required to minimise risk due to construction activities

##### Class I

###### HPR/ Project Manager/Clinical Liaison (CHS)/ FM/ Site Manager (Contractor) responsibilities

Dust control, cleaning and ventilation

Execute work by methods to minimise dust during construction activities

Wear white cotton gloves if moving ceiling tiles and they are to be returned to the correct position immediately after visual inspection. Tiles must not be left displaced.

Daily wipe down of floor with wet mop or vacuum with a HEPA filter

Monitor filters regularly. Clean or change as needed

Wipe horizontal and vertical work surfaces with clean damp cloths using neutral detergent and water

###### HPR/ Project Manager/Clinical Liaison (CHS)/ Facilities Management / Site Manager (Contractor) responsibilities

Hydraulics

Schedule water interruptions during periods of low activity (e.g. evenings/overnight, if possible)

If planned construction disrupts water for greater than 15 minutes, but less than 1 day, run water at each outlet for a minimum of 30 seconds, both hot and cold water at highest velocity possible

Ensure tap aerators are not installed

Observe for discoloured water and water leaks and report to Facilities Management (FM) Log an FM work request

Maintain as dry an environment as possible and report any water leaks that occur to FM and ISAR (or NCH equivalent)

###### HPR/ Clinical Liaison/ Area Manager/ Team Leader responsibilities

Patient risk reduction - Collaboration between HPR and area manager to:

Minimise patient’s exposure to identified hazards and/or relocate most vulnerable patients furthest away from construction area

If possible, coordinate works at non-peak or non-operational times, such as upon discharge or outside clinic hours of operation

Move portable equipment out of construction area

Contact CHS Curator Arts in Health in relation to any art requiring relocation and/or repair Arts in Health

##### Class II

###### HPR/ Project Manager/Clinical Liaison (CHS)/ FM/ Site Manager (Contractor) responsibilities

Dust control, cleaning and ventilation

Execute work using methods to minimise dust during construction activities

Use of drop sheets to control dust

Seal windows and unused doors with duct tape

Seal air-vents and oxygen outlets in construction zone

Sticky mats to be used at both entrance and exit of work area

Daily wipe down of floor with wet mop or vacuum with HEPA filter

Monitor the need to change or clean air filters

Clean all horizontal and vertical surfaces with neutral detergent and water

Isolate HVAC system in areas where work is being undertaken

Plan for construction waste to be transported in tightly covered containers

###### HPR/ Project Manager/Clinical Liaison (CHS)/ FM/ Site Manager (Contractor) responsibilities

Hydraulics

Avoid collection tanks and long pipes that allows water to stagnate

HPR to identify if there is an annual Water Management Plan for the building where construction is occurring. Identify if there is Legionella risk due to previous contamination

If Legionella is known to be in the building where construction is, consider hyper chlorinating or thermal flushing pipes (also known as scorching)

###### HPR/ Clinical Liaison/ Area Manager/Team Leader responsibilities

Patient Risk Reduction - Collaboration between HPR and nursing staff to ensure:

Minimise patient’s exposure or relocate most vulnerable patients furthest away from construction area

If possible, coordinate a time when the area is available such as, upon discharge

Move portable equipment out of construction area

Fixed equipment to be covered with impermeable cover

##### Class III

###### Project Manager (CHS)/Clinical Liaison (CHS)/ Site Manager (Contractor) responsibilities

Dust control, cleaning and ventilation

Execute work using methods to minimise dust during construction activities

Complete all construction barriers before construction begins

Sticky mats to be used at both entrance and exit of work area

Maintain negative air pressure within work site utilising HEPA filtered ventilation units or other methods of maintaining negative pressure

Ensure windows, doors, plumbing penetrations, electrical outlets, intake and exhaust vents are properly sealed with plastic and duct taped within the construction/renovation area

Vacuum air ducts and spaces above ceilings as required

Ensure construction workers wear protective clothing and clean items before entering in patient care areas or public spaces

Dust barriers are not to be removed until the area has been thoroughly cleaned, and the project is complete.

Remove barrier materials carefully to minimise spreading of dirt and debris associated with construction. Barrier material should be wet wiped, HEPA vacuumed, or water misted prior to removal

Increase frequency of cleaning in areas adjacent to the construction zone such as hallways

Ensure air is exhausted directly outside and away from intake vents or filtered through a HEPA

Plan for construction waste to be transported in tightly covered containers

Plan for daily vacuum with HEPA filter to work area

Project manager to design a traffic flow which provides a safe route for construction staff.

Spotters should be assigned when construction staff are on ladders where public traffic pass through

###### Project Manager (CHS)/Clinical Liaison (CHS)/ Site Manager (Contractor) responsibilities

Hydraulics

Schedule water interruptions during periods of low activity (e.g. evenings/overnight, if possible)

Ensure tap aerators are not installed

Observe for discoloured water and water leaks and report to Facilities Management (FM) Log an FM work request

Avoid collection tanks and long pipes that promotes water stagnation

IPAC/ ISAR (or NCH equivalent) to liaise with project manager/ plumber identify historical Legionella issues within the building where construction is occurring

If Legionella is known to be in the building where construction is, consider hyper chlorinating or thermal flushing pipes (also known as scorching)

All taps to run for at least 30 seconds each faucet once per week and this should be recorded by project team (Attachment 4)

Prior to handover all taps to run for at least 30 seconds at maximum velocity, alternating hot and then cold taps

###### Infection Prevention and Control responsibilities

IPAC to review Disturbance or Interference with Services, Safety or Traffic (DISST) application, provide recommendations prior to hoarding and complete Infection Prevention and Control Risk Assessments – Pre-construction, Site Inspections and End of Construction Checklist

IPAC to review workflow pattern so construction workers can enter and exit the construction zone safely. Consideration should be given to sterile supplies and stock that cannot be moved due to storage requirements as per AS5369:2023

IPACU to support the project and provide advice to ensure construction aligns with the principles set out in the AusHFG

IPAC to assess requirements for water or air sampling with project manager

CHS staff are not permitted to visit the construction site unless invited by project manager

CHS staff are to comply with dress code for site visit as stipulated by the project manager. This may include steel capped boots, safety glasses, high vis vest and hard hat. Staff are to ensure footwear is clean after leaving construction zone.

##### Class IV

###### Project Manager (CHS)/Clinical Liaison (CHS)/ Site Manager (Contractor) responsibilities

Dust control, cleaning and ventilation

Complete all construction barriers before construction begins

Maintain negative air pressure within work site utilising HEPA filtered ventilation units or other methods of maintaining negative pressure

Seal holes, pipes, conduits, and punctures to prevent dust migration

Construct anteroom and require all personnel to pass through the room.

Sticky mats to be used at both entrance and exit of work area

Wet mop or HEPA vacuum anteroom daily

During demolition, dust producing work, or work in the ceiling, disposable shoes and coveralls are to be worn and removed in the anteroom when leaving work area

Increase frequency of cleaning in areas adjacent to the construction zone such as hallways

Ensure air is exhausted directly outside and away from intake vents or filtered through a HEPA

Plan for construction waste to be transported in tightly covered containers

Plan for daily vacuum with HEPA filter to work area

Project manager to design a traffic flow which provides a safe route for construction staff.

Spotters should be assigned when construction staff are on ladders where public traffic pass through

Remove barrier materials carefully to minimise spreading of dirt and debris associated with construction. Barrier material should be wet wiped, HEPA vacuumed, or water misted prior to removal

###### Project Manager (CHS)/ Clinical Liaison (CHS)/Site Manager (Contractor) responsibilities

Hydraulics

Schedule water interruptions during periods of low activity (e.g. evenings/overnight, if possible)

Ensure tap aerators are not installed

Observe for discoloured water and water leaks and report to Facilities Management (FM)

Avoid collection tanks and long pipes that allows for stagnation of water and terminate dead legs at the water source.

IPAC/ISAR to liaise with project manager/ plumber identify historical Legionella issues within the building where construction is occurring

If Legionella is known to be in the building where construction is, consider hyper chlorinating or thermal flushing pipes (also known as scorching)

All taps to run for at least 30 seconds each faucet once per week and this should be recorded by project team (Attachment 4)

Prior to handover all taps to run for 30 at least seconds, alternating hot and then cold taps

###### Infection Prevention and Control and Infrastructure Safety and Risk (or NCH equivalent) co- responsibilities

IPAC to review DISST application and provide any IPAC recommendations prior to hoarding

IPAC and ISAR to liaise with project manager to formulate a designated traffic pattern so construction workers can enter and exit the construction zone safely. Consideration should be given to sterile supplies and stock that cannot be moved due to storage requirements as per AS5369:2023

IPAC will liaise with project manager or site manager to ensure infection prevention measures are in place

IPAC to support the project manager by providing advice to ensure construction aligns with the principles set out in the AusHFG

IPAC in consultation with ISAR, to provide recommendations for water and/or air sampling with the project manager

Back to Contents

#### Section 3 – Harmful Pathogens

##### 3.1 Mould

Moulds, such as Aspergillus species, are spore-forming filamentous fungi commonly found within the natural environment, but particularly in moist, damp areas and in soil and vegetable matter, such as mulch. Spores can remain undetected and dormant until disturbed during demolition and construction activities. Once disturbed tiny spores are dispersed into the air and can be inhaled. People are frequently exposed to fungal spores in the environment and do not experience any adverse effects, as the body successfully eliminates the spores. In immunocompromised people (often present in healthcare facilities) fungi can grow within the sinuses and/or lungs and then invade through the bloodstream to other organs, such as the brain. Aspergillus species are the predominant cause of invasive mould infections in humans, however other fungal species have the potential to cause infection and disease, particularly in immunocompromised patients 4.

People who are particularly vulnerable to invasive fungal infections 5 include:

Oncology or chemotherapy patients

Haematology malignancy and stem cell transplant patients

Solid organ transplant patients

Patients with cystic fibrosis

Premature babies

Any person who is moderately to severely immunocompromised

##### 3.2 Legionella

Legionella pneumophila and Legionella longbeachae are bacteria responsible for the illness known as Legionellosis or Legionnaires Disease. Legionella pneumophilia is found in low levels in the natural environment and thrives in warm water temperatures less than 60°C 6.

Legionella species are transmitted via inhalation of aerosols or aspiration of contaminated water 7.

Healthcare associated Legionnaires’ disease is predominantly due to micro aspiration of contaminated water into the lungs 5.

Legionella species may affect and cause severe disease in critically vulnerable patients 7 including:

Immunocompromised patients (oncology, haematology, stem cell recipients, organ transplant recipients or any person on immunosuppressive medication)

Chronic disease patients (diabetes mellitus, chronic obstructive pulmonary disease, congestive heart failure, liver failure)

Patients who have recently undergone surgery

Intubated and mechanically ventilated patients

Patients receiving fluids via nasogastric feeding who are at higher risk of aspiration.

Note: Hospital acquired pneumonia in the setting of detection of Legionella, is covered in the CHS Infection Prevention and Control Procedure, Canberra Hospital building specific Water Management Plans (Canberra Hospital FM), or NCH Water Management Plan available through Healthhub.

Back to Contents

#### Section 4 – Management of Mould

All unexpected mould finds will activate the Canberra Hospital Mould Working Group (or NCH equivalent), comprised of ISAR (or NCH equivalent), IPAC, ACT Pathology Microbiology and Facilities Management (FM).

Delays in mould remediation can compromise patient, staff and visitor safety 5 and adversely affect the operational requirements of CHS Network.

##### 4.1 Investigation of water intrusion

Water damage and mould growth can arise from various causes such as leaks, steam/condensate build-up, intrusion from rainwater or leaking hydraulic pipes. 8

The immediate priority should be to stop the leak. Evaluation will include:

Whether dampness is new, recurrent or chronic

Determine the extent and type of water intrusion (black, grey, potable or stormwater)

Determine the human risk in the occupied space

Evaluating the extent of mould can be complex due to the variation of growth on porous and non-porous material and areas where mould can remain hidden such as under vinyl or between floor levels.9

##### 4.2 Investigation of water damage or mould find during construction activities

While the engaged principal contractor may control the construction site via a formal site possession, it is essential for the site manager and CHS project representative/manager to inform ISAR (or NCH equivalent) and IPAC about any instances of uncontrolled water intrusion, water damage or mould. This ensures that timely and appropriate control measures are implemented to prevent the migration of mould spores to adjacent clinical or public areas.

The construction site manager and CHS HPR can document findings through either a site visit with ISAR and IPAC, and/or comprehensive digital photographs that clearly capture the extent of the damage. Investigations should include a written report outlining the severity of the water damage or mould, along with identifying the source of the water (treated water, wastewater, steam, rain, or groundwater).

In some instances, when informed by ISAR (or NCH equivalent) or IPAC, a qualified Environmental Hygienist Professional (EHP) will be engaged by the contractor to evaluate the extent of the damage, recommend cleaning procedures, and provide a written report to CHS. As part of the investigation, air sampling specifically for mould may be required, as determined by the Canberra Hospital Mould Working Group (or NCH equivalent).

##### 4.3 Reporting an unexpected mould find in a setting not under construction

In the event mould is found or suspected in a CHS facility, a FM work request must be raised, and ISAR (or NCH equivalent) and relevant building Facility Operation Manager (FOM) notified. ISAR (or NCH equivalent) will liaise with the CH Mould Working Group (or NCH equivalent) stakeholders, to assess the impacted area and provide advice to FM to ensure the safety of patients, visitors and staff.

##### 4.4 Assessment of water damage and mould

Mould can be identified or confirmed by the presence of any of the following:

Visible mould growth or visible signs of dampness

Perceived mouldy or earthy odour

Presence of condensation or high humidity - if air handling units (AHUs) are turned off and humidity remains, mould may grow

Historical water damage or mould within the same building or clinical area

Moisture readings performed by an experienced professional. This can be done by experienced ISAR (or NCH equivalent) or FM staff.

##### 4.5 Remediation

The CH Mould Working Group (or NCH equivalent) will be stood up in the instance of large-scale mould findings. The Working Group can provide advice regarding safe management and timely remediation of works involving mould.

ISAR (or NCH equivalent) and IPAC teams will assess the level of risk and employ the appropriate infection prevention and control measures. Cleaning and remediation works must not begin until the moisture source is stopped. It is imperative ISAR (or NCH equivalent) is engaged to provide guidance to the FM/Capital Project Delivery teams and engage an environmental hygienist professional to cleaning and remediating the area. Environmental Hygienists will provide a clearance certification prior to returning the area to operational status.

##### 4.6 Guide to management of moisture affected porous and non-porous materials

| Moisture affected material | Actions |
| --- | --- |
| Books and papers | For non-valuable items, discard books and papers Photocopy valuable/important items, discard originals if mould is visible |
| Carpet and backing – dry within 24 to 48 hours | Remove water with water extraction vacuum Reduce ambient humidity levels with dehumidifier Accelerate drying process with fans |
| Ceiling tiles, gyprock or cellulose, fiberglass insulation | Discard and replace |
| Concrete or cinder block surfaces | Remove moisture with water extraction vacuum Accelerate drying process with dehumidifiers |
| Flooring - vinyl, ceramic tiles | Vacuum or damp wipe with water and mild detergent, scrub if needed and allow to dry |
| Walls - dry wall & gypsum | Can be dried in place if there is no damage to the drywall. If damaged remove, discard and replace Ventilate the wall cavity if possible |
| Art | Framed works should be removed in association with the CHS Curator, Arts in Health and FM for review/repair by the Curator. Vinyl wallpapers on compromised drywall should be discarded with the drywall and replaced once the new support is in place. Contact CHS Curator, Arts in Health for site specific advice and see Infection Prevention and Control Section in the Arts in Health – Asset Management in Canberra Health Services’ Facilities Procedure for more details. |
| Upholstered furniture | Remove moisture with water extraction vacuum Accelerate drying process with dehumidifiers, fans or heaters |
| Hard non-porous surfaces | Vacuum or damp wipe with water and mild detergent, scrubbing is acceptable and allow to dry |
| Window treatments such as roller blinds, venetians, curtains | Clean as per manufacturer’s instructions |
| Porous surfaces such as wood | Remove moisture, use dehumidifiers, low heat and fans. Wood finishes that are treated may be cleaned with mild detergent and left to dry Wet panels are to be removed to allow for maximum drying |
| Laminate | Laminate surfaces that are well maintained should be water resistant, but chips, crack and dents can lead to moisture permeating under the laminate layer. Joinery on furniture affected by water damage or mould should be reviewed and disposed of if necessary. |
| Electrical | Consider all electrical items exposed to moisture as potential shock hazards. This includes wiring, light fixtures, switch boards, motors that require an electrician to check the electrical safety |

If there is doubt regarding removal of items, please contact IPAC/ISAR or NCH equivalent:

CHSIPCU@act.gov.au

CHSNCH.Infectioncontrol@act.gov.au

Safetyandrisk@act.gov.au

Back to Contents

#### Section 5 – Microbial and air particle sampling

The physical environment in healthcare facilities can serve as a reservoir for microbial growth.  Microbial and air particle sampling are supplemental strategies used to monitor and assess the effectiveness of the construction risk management strategies in high-risk areas. 10

Microbial and air particle sampling are required prior to commissioning of all new builds and following major renovations in high-risk locations. 1,11

Microbial sampling involves directly sampling a specified volume of air onto an agar plate to culture for fungi (mould) and bacteria (active sampling).

Air particle sampling differentiates various size particles within a specified volume of air. Air particle sampling does not identify microbes within the air, however, provides an immediate indication of potential breaches in dust control measures and/or malfunctioning HEPA filters.

##### 5.1 Indications for microbiological air sampling within a CHS facility

Mandatory

During the commissioning of new facility and following refurbishment/renovation of the following locations (prior to “Go live”).

Operating theatres

Sterile stockrooms/storerooms

Pharmacy laboratories

Sterilising Services Unit (SSU)

Isolated NICU operating theatre with HEPA

Sterile stock rooms that have HEPA ventilation

Other high-risk HEPA filtered positive pressure rooms (e.g. haematology)

A risk assessment should be undertaken, and testing considered for all other construction activity (refer to Section 2, Table 1).

Testing is not required for routine HEPA filter changes.

##### Considered

During Type C or D construction or renovation which involves highest risk infection control groups, such as:

Haematology

Oncology

Transplant Units

Radiation and Chemotherapy Outpatients

Angiography

Sterile supply units

Pharmacy - Clean rooms/Admixture

Interventional radiology

Operating theatres and

During investigation and management of mould contamination

Around construction sites that are adjacent to highest risk-high risk patient groups

##### 5.2 Microbial air sampling methodology

There are no national or international standards for sampling, processing and reporting of microbial air samples 11.  Methods may vary depending on the area being sampled and reason for sampling.

IPAC and ACT Pathology-Clinical Microbiology are available to provide information, guidance and advice regarding indication, methodology and interpretation of results for air sampling. The clinical significance of the location within the health care facility and the patient’s risk profile should be established swiftly and communicated to the testing facility on the pathology order form.

Active sampling is the preferred method for air sampling at CHS.  For commissioning/re-commissioning of HEPA filtered rooms, active air sampling requires the area to conform to operational conditions, such as air handling units (AHU) operating continuously for 24 hours prior to sampling to ensure the required humidification, and air exchanges have been achieved.  All activity should be restricted within the room for 24 hours before and during sampling.

CHS require air sampler machines to follow the manufacturer’s instructions for use, including scheduled maintenance and calibration.  CHS require all samples to be analysed by a National Association of Testing Authorities (NATA) laboratory, accredited to undertake environmental testing.

The following results should be expected in HEPA filtered rooms:

Total mould count (including Aspergillus species): less than1 CFU/m3

Total bacterial count: less than or equal to 10 CFU/m3

Results outside of these parameters must be notified to IPCU/ACT Pathology Microbiology and appropriate actions undertaken (e.g. clinical re-cleaning, review of sampling technique, review of controls measures) prior to re-sampling, and prior to the area being returned to operational status.

Limits for other settings are not well defined and will be determined on a case-by-case basis in consultation with IPAC/ACT Pathology Microbiology prior to testing.

Test results are to be sent to IPAC and ISAR (or NCH equivalent) and project managers

IPCU  CHSIPCU@act.gov.au

ISAR (or NCH equivalent) safetyandrisk@act.gov.au

North Canberra Hospital and Clare Holland House chsnch.infectioncontrol@act.gov.au

Note: Testing can take up to 7 days to have results returned. Commissioning/recommissioning cannot occur before results are finalised.

##### 5.3 Air particle sampling

There are no specific standards for air particle sampling within non-pharmaceutical areas of healthcare facilities.  There are international standards for cleanrooms.  ISO 7 (ISO-14644-1:2015) is a common clean cleanroom classification (e.g. pharmacy compounding rooms, medical device manufacturing with 60 HEPA filtered air changes per hour) which may be considered similar environments to high-risk HEPA filtered rooms in healthcare facilities.

Air particle sampling is mandatory when commissioning a new build or following a renovation of a high-risk location 1,12

Air particle sampling is also used to ensure control measures, particularly dust controls are effective. IPAC and Clinical Microbiology can assist with suggested sampling regimes of areas requiring monitoring.

ISO 7 (ISO-14644-1:2015) defines the following limits per m3 of air sampled:

352,000 (0.5 microns)

83,200 (1 micron)

2930 (5 microns)

Results over these parameters indicate a requirement to tighten control measures prior to re-sampling.

Back to Contents

#### Section 6 – Record Management

ISAR (or NCH equivalent) and IPAC are responsible for maintaining infection control risk assessment and monitoring documentation throughout the life of the project. In certain circumstances, records must be kept by ISAR and IPAC as evidence of policy implementation. ISAR and IPAC will also determine the appropriate length of time for retaining these records.

Back to Contents

#### Evaluation

##### Outcome

All construction and maintenance activities are conducted safely and appropriately, minimising the risk of infection to patients, visitors, contractors, and staff.

##### Measures

Review of legionella infections contracted at CHS.

Review of IPCRA reports to ensure they are recording required information.

Back to Contents

#### Related policies, procedures, guidelines and legislation

##### Policies

- Work Health Safety

- Partnering with Consumers

- Risk Management

- Waste Management

##### Procedures

Infection Prevention and Control

Preventing and Controlling Healthcare Associated Infections

Arts in Health – Asset management in Canberra Health Services Facilities

##### Guidelines

Risk Management

CHS Water Management plan

NCH Water Management plan

##### Legislation

Health Records (Privacy and Access) Act 1997

Human Rights Act 2004

Work Health and Safety Act 2011

Work Health and Safety Regulations 2011

Public Health Act 1997

Health Facility Code of Practice 2021

Work Health and Safety(How to manage work health and safety risks) Code of Practice 2020

Carers Recognition Act 2021

##### Other

Australian Charter of Healthcare Rights

CHS Facilities Management Standard Inclusions

NCH Facilities Management Standard Inclusions

CHS Architectural Standard Inclusions

CHS Hydraulic Standard Inclusions

CHS DISST Procedure

ACT Pathology – Manuals - Air Sampling

Standards Australia, Waters – Examination for legionellae (AS3896:1991)

Standards Australia, Reprocessing of reusable medical devices (AS5369:2023)

Standards ISO, Clean rooms and associated controlled environments (ISO-14644-1:2015)

Back to Contents

#### References

Australasian Health Infrastructure Alliance (AHIA), 2025, Australasian Health Facility Guidelines – Part D Infection Prevention and Control, AusHFG | (healthfacilityguidelines.com.au)

Infection Control Principles for the Management of Construction, Renovation, Repairs and Maintenance within Health Care Facilities. A Manual for Reducing the Risk of Health Care Associated Infection by Dust and Water Borne Micro-organisms. Second Edition. 2005. Accessed 4 May. https://content.health.vic.gov.au/sites/default/files/migrated/files/collections/policies-and-guidelines/c/constructionrenovationrepairsmaintenanceinhealthcf---pdf.pdf

Australian Commission on Safety and Quality in Health Care. National Safety and Quality Health Service Standards. 2nd ed. – version 2. Sydney: ACSQHC; 2021

Thompson, G.R., Young, J. H. Aspergillus Infections. New England Journal of Medicine (2021) 395: 1945-1609. Available from: Aspergillus Infections | NEJM

Health protection Surveillance Centre.  National guidelines for the prevention of nosocomial aspergillosis.  January 2018. Ireland.

enHealth (2015). Guidelines for Legionella control in the operation and maintenance of water distribution systems in health and aged care facilities. Australian Government, Canberra. Available at: enHealth guidance – Guidelines for Legionella control

New South Wales Legionnaires’ disease control guideline. Control Guidelines for Public Health Units (2023) Available from : Legionnaires' disease control guideline - Control guidelines (nsw.gov.au)

SF2H SFMM Risk of fungal infections and construction work in hospitals.  Identification of risks and implementation of management precautions. March 2011.

World Health Organization (WHO). WHO Guidelines for indoor air quality: dampness and mould (2009). Available at:  9789289041683-eng.pdf

Morris G, Kokki MH, Anderson K, Richardson MD.  Sampling of Aspergillus spores in air.  J Hosp Infect. 2000;44:81-92.

Microbiological air sampling of operating rooms in Western Australian healthcare facilities. Communicable Disease Control Directorate Guideline.  Government of Western Australia Guideline 0003/December 2024.

Government of South Australia. Infection prevention and control during construction and renovation: Toolkit (2018) Available from: SA Health Report Template - Blue and White - Helix Position A

- Back to Contents

#### Definition of terms

Air sampling: The collection and analysis of samples of air to measure the amounts of various pollutants or other substances in the air. Routine air sampling involves equipment which draws air volume into a cassette for testing.

CFU/m3: Colony forming units per cubic metre- a measure of the amount of bacterial or fungal growth

CFU: colony forming unit:  a unit of measurement which estimates the number of microbial cells (bacteria, fungi, viruses) in a sample that are viable

Construction Activity Type: Construction activity type is defined by the amount of dust that is generated, the duration of the activity and any impact on the Heating/Ventilation/Air Conditioning (HVAC) systems

Construction: Construction work is defined as any work carried out in connection with the construction, alteration, conversion, fitting-out, commissioning, renovation, repair, maintenance, refurbishment, demolition, decommissioning or dismantling of a structure.

Cooling tower: a device for lowering the temperature of water by evaporative cooling in which atmospheric air is in contact with falling water thereby exchanging heat. Evaporative condenser a heat exchanger in which refrigerant is cooled by a combination of air movement and water spraying.

Demolition: Tearing down of buildings or other structures

Dust: Particles in the atmosphere that come from various sources

Fungal spores: The main reproductive unit of fungi which disseminate in the air and cause infection in humans

HEPA: High Efficiency Particulate Filtration of 99.95% efficiency > 10 air changes per hour

Immunocompromised person: a person who has impaired ability to fight off infection

Infection: The invasion of the body by pathogenic microorganisms that reproduce and multiply, causing disease by local cellular injury, secretion of a toxin or antigen-antibody reaction to the host

Microbe: tiny form of life which can be bacterial, viral or fungal that may be capable of causing infection or disease

Mould: The colloquial term mould is applied to a large and taxonomically diverse number of fungal species where their growth results in a mouldy appearance of objects

Renovation: (also called remodelling) is the process of improving a structure

Back to Contents

#### Search terms

Construction, renovation, maintenance, infection control, risk assessment, compliance, legionella, mould, bacteria, water, flushing.

- Back to Contents

#### Attachments

Attachment 1 - IPCRA - Pre-construction – Class IIV

Attachment 2 - IPCRA  Site inspection record

Attachment 3 - IPCRA - End of construction checklist

Attachment 4 - Weekly flushing schedule

Attachment 5 - Water sampling information guide

- Back to Contents

For Policy Team to complete:

| Date amended | Section amended | Divisional approval | Final approval |
| --- | --- | --- | --- |
| 28 October 2025 | New document | Chris Tarbuck, Executive Group Manager, IHSS | CHS Policy Document Review Panel |
| 27 January 2026 | Minor formatting changes made to meet accessibility requirements | CHS Policy and Consumer Handouts Team | CHS Policy and Consumer Handouts Team |

This document supersedes the following:

| Document number | Document name |
| --- | --- |

Disclaimer

This document has been developed by Canberra Health Services specifically for its own use.  Use of this document and any reliance on the information contained therein by any third party is at his or her own risk and Canberra Health Services assumes no responsibility whatsoever.

- Back to Contents

| Acknowledgement of Country Canberra Health Services acknowledges the Ngunnawal people as traditional custodians of the ACT and recognises any other people or families with connection to the lands of the ACT and region. We acknowledge and respect their continuing culture and contribution to the life of this region. © Australian Capital Territory, Canberra 2024 | Accessibility call (02) 5124 0000 Interpreter call 131 450 canberrahealthservices.act.gov.au/accessibility |
| --- | --- |

#### Attachment 1 – IPCRA – Prior to Construction

| ##### Project details and infection control measures |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Project Name/ DISST (if applicable) | Click here to enter text. |  |  |  |  |  |  |
| Contractor Information | Company Name: Click here to enter text. |  |  |  |  |  |  |
| CHS Project Representative | Name: Click here to enter text. Position: Click here to enter text. |  |  |  |  |  |  |
| Persons Involved in Risk Assessment | ☐ Infrastructure and Health Support Click here to enter text. ☐ Infection Prevention and Control: Click here to enter text. ☐ Contractor: Click here to enter text. ☐ Work Health and Safety: Click here to enter text. ☐ Health Project Representative: Click here to enter text. |  |  |  |  |  |  |
| Date of Risk Assessment: | Click here to enter a date. |  |  |  |  |  |  |
| Work Order/Contract number: | Click here to enter text. |  |  |  |  |  |  |
| Location of Work: | Click here to enter text. |  |  |  |  |  |  |
| Construction Activity Type: | ☐ Type A |  | ☐ Type B |  |  | ☐ Type C | ☐ Type D |
| Patient Risk Group | ☐ Low |  | ☐ Medium |  |  | ☐ High | ☐ Highest |
| Class of Infection Protection Control Measures Required | ☐ Class I |  | ☐ Class II |  |  | ☐ Class III | ☐ Class IV |
| Infection control measures prior to beginning project |  |  |  |  |  |  |  |
| ###### Secondary Approvals/Considerations (Completed by Permit to Work Initiator and/or Acceptor) |  |  |  |  |  |  |  |
| DISST Approval |  | Yes |  | No | NA Reason: |  |  |
| Window opening Permit |  | Yes |  | No | NA Reason: |  |  |
|  |  | Yes |  | No | NA Reason: |  |  |

| Infection Prevention and Control measures Class I-IV | APPLICABLE |
| --- | --- |
| Project presented to DISST | Yes/No/Comment |
| Work methods are used to minimise dust | Yes/No/Comment |
| If ceiling tiles are removed for the purpose of inspection they are replaced immediately | Yes/No/Comment |
| Work area is damp mopped/ vacuumed each day using HEPA filter filtration vacuum | Yes/No/Comment |
| Cleaning of vertical and horizontal surfaces such as benches | Yes/No/Comment |
| Daily waste removal via assigned pathways | Yes/No/Comment |
| Traffic flow is managed to prevent/ reduce patient or public access | Yes/No/Comment |
| Use of spotters for technicians using ladders | Yes/No/Comment |
| Wet mop or HEPA vacuum twice per day of work site | Yes/No/Comment |
| In construction zone where containment is not possible (No ante room) one of the following is applied: a). Airtight plastic barriers (e.g., Zipwall system) extending from floor to true ceiling b). Plastic barriers with seams sealed with duct tape | Yes/No/Comment |
| Patient care equipment removed or covered and protected from dust | Yes/No/Comment |
| Flush water lines prior to use & observe for discoloured water | Yes/No/Comment |
| Check that aeration ends are not on taps- Laminar flow should be achieved | Yes/No/Comment |
| IPC or ISAR Officer to be supplied construction plans | Yes/No/Comment |
| Work methods are used to minimise dust | Yes/No/Comment |
| In construction area, HVAC is isolated | Yes/No/Comment |
| Public access is diverted away from construction | Yes/No/Comment |
| Use of sticky mats | Yes/No/Comment |
| Use of extractor fans | Yes/No/Comment |
| Plan in place for extractor fan filters to be changed/ cleaned as required | Yes/No/Comment |
| Drop sheets to control dust | Yes/No/Comment |
| Water mist work surfaces to control dust while cutting | Yes/No/Comment |
| If possible, maintain negative pressure in construction area | Yes/No/Comment |
| Windows and unused doors are sealed | Yes/No/Comment |
| Air vents including intake and exhaust vents and oxygen outlets are sealed | Yes/No/Comment |
| Plumbing penetrations sealed such as drains and sinks | Yes/No/Comment |
| Construction waste is not disposed of in general rubbish | Yes/No/Comment |
| Planned daily removal of construction waste to be contained and secured in covered containers | Yes/No/Comment |
| Assess risk of water stagnation in long pipes and dead leg (refer to relevant water management plan for specific area/ building) | Yes/No/Comment |
| Confirm with project manager installation of taps will have laminar flow and without aeration fittings | Yes/No/Comment |
| Planned weekly flushing of under utilised faucets, hot and cold for a minimum of 30 seconds each (document on template) | Yes/No/Comment |
| Discuss with project manager contingency plan in the event of discolouration of water or water intrusion or visible mould | Yes/No/Comment |
| Requirement for pre- construction environmental sampling | Yes/No/Comment |
| Based on the construction location, discuss with project manager if air or water sampling is required to be arrange at end of construction. Note: high risk areas such as theatres or clean areas including pharmacy require air sampling upon completion of works and after HVAC has resumed for minimum of 24 hours continuously | Yes/No/Comment |

A copy of this risk assessment must be forwarded to the Health Project Representative and ISAR (or NCH equivalent) safetyandrisk@act.gov.au to be kept on file.

Additional comments:

- Back to Contents

#### Attachment 2 – IPCRA – Site Inspection Record

| ##### Project details and infection control measures |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Project Name/ DISST (if applicable) | Click here to enter text. |  |  |  |  |  |  |
| Contractor Information | Company Name: Click here to enter text. |  |  |  |  |  |  |
| CHS Project Representative | Name: Click here to enter text. Position: Click here to enter text. |  |  |  |  |  |  |
| Persons Involved in Risk Assessment | ☐ Infrastructure and Health Support: Click here to enter text. ☐ Infection Prevention Control: Click here to enter text. ☐ Contractor: Click here to enter text. ☐ Work Health and Safety: Click here to enter text. |  |  |  |  |  |  |
| Date of Risk Assessment: | Click here to enter a date. |  |  |  |  |  |  |
| Work Order/Contract number: | Click here to enter text. |  |  |  |  |  |  |
| Location of Work: | Click here to enter text. |  |  |  |  |  |  |
| Construction Activity Type: | ☐ Type A |  | ☐ Type B |  |  | ☐ Type C | ☐ Type D |
| Patient Risk Group | ☐ Low |  | ☐ Medium |  |  | ☐ High | ☐ Highest |
| Class of Infection Protection Control Measures Required | ☐ Class I |  | ☐ Class II |  |  | ☐ Class III | ☐ Class IV |
| Infection control measures prior to beginning project |  |  |  |  |  |  |  |
| ##### Secondary Approvals/Considerations (Completed by Permit to Work Initiator and/or Acceptor) |  |  |  |  |  |  |  |
| DISST Approval |  | Yes |  | No | NA Reason: |  |  |
| Window opening Permit |  | Yes |  | No | NA Reason: |  |  |
|  |  | Yes |  | No | NA Reason: |  |  |

| Construction Barricade |  |  |  |
| --- | --- | --- | --- |
| Dust tight barricades sealed, no penetration | Yes | No | NA |
| Dust mats at entrance/exit | Yes | No | NA |
| All access doors close and sealed properly | Yes | No | NA |
| All access doors are closed to the public | Yes | No | NA |
| Adjacent areas with staff / patient access |  |  |  |
| Ceiling areas intact and dry | Yes | No | NA |
| Floor areas clean with no dust tracked | Yes | No | NA |
| Walls intact and dry | Yes | No | NA |
| Horizontal surfaces dust free | Yes | No | NA |
| Vents dust free | Yes | No | NA |
| All ventilation ducts from building site sealed | Yes | No | NA |
| No signs of pest infection | Yes | No | NA |
| Traffic Flow |  |  |  |
| Building contractor accessing site through approved non-patient care areas | Yes | No | NA |
| Waste covered and contained prior to removal | Yes | No | NA |
| Routine and timing of waste removal as per DISST | Yes | No | NA |
| Air or water sampling required (circle) | Yes | No | NA |

Comments:

A copy of this IPCRA must be forwarded to the Health Project Representative and ISAR (or NCH equivalent) on safetyandrisk@act.gov.au and kept on file.

#### Attachment 3 – IPCRA – End of Construction Checklist

| ##### Project details and infection control measures |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Project Name/ DISST (if applicable) | Click here to enter text. |  |  |  |  |  |  |
| Contractor Information | Company Name: Click here to enter text. |  |  |  |  |  |  |
| CHS Project Representative | Name: Click here to enter text. Position: Click here to enter text. |  |  |  |  |  |  |
| Persons Involved in Risk Assessment | ☐ Health Infrastructure Services: Click here to enter text. ☐ Infection Protection Control: Click here to enter text. ☐ Contractor: Click here to enter text. ☐ Work Health and Safety: Click here to enter text. |  |  |  |  |  |  |
| Date of Risk Assessment: | Click here to enter a date. |  |  |  |  |  |  |
| Work Order/Contract number: | Click here to enter text. |  |  |  |  |  |  |
| Location of Work: | Click here to enter text. |  |  |  |  |  |  |
| Construction Activity Type: | ☐ Type A |  | ☐ Type B |  |  | ☐ Type C | ☐ Type D |
| Patient Risk Group | ☐ Low |  | ☐ Medium |  |  | ☐ High | ☐ Highest |
| Class of Infection Protection Control Measures Required | ☐ Class I |  | ☐ Class II |  |  | ☐ Class III | ☐ Class IV |
| Infection control measures prior to beginning project |  |  |  |  |  |  |  |
| ##### Secondary Approvals/Considerations (Completed by Permit to Work Initiator and/or Acceptor) |  |  |  |  |  |  |  |
| DISST Approval |  | Yes |  | No | NA Reason: |  |  |
| Window opening Permit |  | Yes |  | No | NA Reason: |  |  |
|  |  | Yes |  | No | NA Reason: |  |  |

| Do not remove barriers from work area until completed project is inspected by IPC and ISAR and is thoroughly cleaned | Yes | No | NA |
| --- | --- | --- | --- |
| Construction site clean has been conducted. This includes all horizontal and vertical surfaces to ensure all dust and debris has been removed. | Yes | No | NA |
| Wet mop and / or vacuum with HEPA filtered vacuums work site | Yes | No | NA |
| Wet mop and / or vacuum with HEPA filtered vacuums before leaving the work area | Yes | No | NA |
| Remove isolation of HVAC system in areas where work is performed | Yes | No | NA |
| Fogging of HVAC ducting has been completed | Yes | No | NA |
| HEPA filters and laminar/clean flow systems (where installed) have been recertified | Yes | No | NA |
| Flushing schedule records maintained (if required) | Yes | No | NA |
| Air sampling or water sampling required Note: high risk areas such as theatres or clean areas including pharmacy require air sampling upon completion of works and after HVAC has resumed for minimum of 24 hours continuously | Yes | No | NA |

A copy of this risk assessment must be forwarded to the Health Project Representative and ISAR (or NCH equivalent) at safetyandrisk@act.gov.au and to be kept on file.

Any remedial action required to achieve clearance:

Note: Only once clearance is achieved can barrier materials be carefully removed to minimise spreading of dust and debris associated with work activity

#### Attachment 4 – Weekly Flushing Schedule

##### Weekly Flushing Schedule

Hot and cold taps must be flushed on high velocity for a minimum of 30 seconds once per week, to prevent stagnation and biofilm development within hydraulic systems during maintenance and construction activities.

(Insert project name and room identification)

| Date | Flushing completed by – insert name | Next flushing due |
| --- | --- | --- |

#### Attachment 5 – Water Sampling Information Guide

##### Water sampling requirements following construction and refurbishment.

Approved contractors of construction, renovation and maintenance at Canberra Health Services, are required under the Infection Control and Prevention Risk Assessment (IPCRA), Australian Health Facility Guidelines, Part D - Infection Prevention and Control (2025) and Australian and New Zealand Standard 3500 Plumbing and Drainage, to coordinate water sampling (by an approved provider) of identified areas, prior to the commissioning or recommissioning of the work site.

##### Background

Construction, renovations and refurbishments pose many risks when undertaken in the healthcare environment. Risk management strategies and infection controls practices are enacted to ensure patient safety is not compromised.

Underutilised hydraulic systems are at higher risk of stagnation. This stagnation promotes growth of potentially harmful pathogens such as Legionella and Pseudomonas Spp. Extended periods of time without suitable flushing can also be attributed to biofilm development within hydraulic systems. Biofilm development in hydraulic systems make cleaning and disinfecting difficult, and often ineffective. In many cases assets will require costly replacements.

Water outlets that are identified as being unused or underutilised in the IPCRA – Pre-construction are managed by scheduling routine flushing, which must be recorded when undertaken. This strategy however useful is not always appropriate, as sinks with sensor taps are unable to be flushed when the power is cut to distribution boards serving areas within the work site.

##### Requirements

As the overarching control measure to ensure patient safety, all new constructions, and any Type C or D construction in highest risk locations must conduct water sampling prior to recommissioning of the work site to align with AS/NZS3500 and CHS requirements. A certification must be issued to the Project Manager and distributed to ISAR (or NCH equivalent) and IPAC prior to handover.

Contractors can engage any chosen service provider. Canberra Health Services are currently engaged with Hydro Industries, who conduct regular monitoring of operational sites and are familiar with Canberra Hospital Campus. As a current sub-contractor Hydro Industries are registered and compliant with Rapid Global and have already undertaken CHS Induction.

##### Hydro Industries

##### Dave De Silva – 0459 975 178 or ddesilva@hydroindustries.com.au

When booking water sampling, sub-contractors will need to know how many water outlets are to be tested. This includes all sinks including scrub sinks and showers. Please note that water sampling results will take a minimum 7 days to be returned, and if treatment and retesting is required, a likely further 7 days. These timelines should be noted when booking to maintain deadlines and timely project handover.

##### Contractors are responsible for the costs associated with water sampling.

Should you require any further information, please email the relevant Infection Control Unit

CH Infection Prevention and Control Unit – CHSIPCU@act.gov.au

NCH Infection Control - CHSNCH.Infectioncontrol@act.gov.au